Sample Specification 3800

Joint Restraint to prevent axial separation shall be incorporated into the

design of the sleeve or coupling used to connect two plain pipe ends.

The restraint mechanism shall consist of a plurality of individually

actuated gripping surfaces to maximize restraint capability. Torque

limiting twist off nuts shall be used to insure proper actuating of the

restraint devices. The restraint devices shall be coated using MEGABOND

™. (For complete specifications on MEGA-BOND visit

www.ebaa.com.) Ductile Iron components shall be of a minimum of 65-

45-12 ductile iron meeting the requirements of ASTM A536 of the

latest revision and shall be tested in accordance with the stated standard.

The restrained joining system shall meet the applicable requirements

of AWWA C219, ANSI/AWWA C111/A21.11, and ASTM D2000. The

restrained joining system shall be the EBAA Iron Series 3800 or approved

equal.

All EBAA products intended for installation on ductile iron pipe are designed for and limited to use on ductile iron pipes that comply with the requirements of ANSI/AWWA C151/A21.51 and have a Brinell Hardness or equivalent measurement value that does not exceed 230BHN. These requirements apply to the entire pipe wall profile at all restraining wedge engagement points and to the full penetration depth of each restraining wedge.*

*To learn more about this addendum, please visit: https://ebaa.com/spec/dip