Sample Specification Ex-Tend 200

Expansion joints shall be installed in the locations indicated

on the drawings and shall be manufactured of ductile iron

conforming to the material properties of ANSI/AWWA

C153/A21.53. All expansion joints shall be capable of

expanding or contracting to the amounts shown on the

drawings, or indicated in the specifications, but in no case

shall there be less than 4" total axial movement. Separation beyond

the maximum extension of the expansion joint shall be

prevented without the use of external tie rods. Each expansion

joint shall be pressure tested against its own restraint to a

minimum of 350 psi (250 psi 24 inch and greater). MEGALUG

joint restraint shall be provided with each mechanical joint

connection. All pressure containing parts shall be lined with a

minimum of 15 mils of fusion bonded epoxy, conforming to

the applicable requirements of ANSI/AWWA C213, and shall

be tested with a 1500 volt spark test conforming to stated

specification. All expansion joints shall be EX-TEND 200, as

manufactured by EBAA Iron, Inc., or approved equal.