Sample Specification 2100

- Restrained flange adapters shall be used in lieu of threaded, or welded, flanged spool pieces. Flange adapters shall be made of ductile iron conforming to ASTM A536 and have flange bolt circles that are compatible with ANSI/AWWA C110/A21.10.

- Restraint for the flange adapter shall consist of a plurality of individual actuated gripping wedges to maximize restraint capability. Torque limiting actuating screws shall be used to insure proper initial set of gripping wedges.

- The flange adapter shall be capable of deflection during assembly, or permit lengths of pipe to be field cut, to allow a minimum of 0.6” gap between the end of the pipe and the mating flange without affecting the integrity of the seal.

- For PVC pipe, the flange adapter will have a pressure rating equal to the pipe.

- For ductile iron pipe, the flange adapter shall have a safety factor of 2:1 minimum.

- The flange adapter shall be the SERIES 2100 MEGAFLANGE adapter, as produced by EBAA Iron, Inc., or approved equal.

- All EBAA products intended for installation on ductile iron pipe are designed for and limited to use on ductile iron pipes that comply with the requirements of ANSI/AWWA C151/A21.51 and have a Brinell Hardness or equivalent measurement value that does not exceed 230BHN. These requirements apply to the entire pipe wall profile at all restraining wedge engagement points and to the full penetration depth of each restraining wedge.*

Traceability

- An identification number consisting of year, day, plant and shift (YYDDD)(plant designation)(Shift number), shall be cast into each gland body.

- All physical and chemical test results shall be recorded such that they can be accessed via the identification number on the casting.  These Material Traceability Records (MTR’s) are to be made available, in hard copy, to the purchaser that requests such documentation and submits his gland body identification number.

- Production pieces that are too small to accommodate individual numbering, such as fasteners and wedges, shall be controlled in segregate inventory until such time as all quality control tests are passed.  These component parts may then be released to a general inventory for final assembly and packaging.

- All components shall be manufactured and assembled in the United States.  The purchaser shall, with reasonable notice, have the right to plant visitation at his/her expense.

MEGA-BOND® Restraint Coating System

Coating for restraint devices shall consist of the following:

- All wedge assemblies and related parts shall be processed through a phosphate wash, rinse and drying operation prior to coating application. The coating shall consist of a minimum of two coats of liquid thermoset epoxy coating with heat cure to follow each coat.

- All casting bodies shall be surface pretreated with a phosphate wash, rinse and sealer before drying. The coating shall be electrostatically applied and heat cured. The coating shall be a polyester based powder to provide corrosion, impact and UV resistance.

- The coating system shall be MEGA-BOND by EBAA Iron, Inc. or approved equal. Requests for approved equal must submit coating material and process details for review prior to bid.

- For more information regarding MEGA-BOND, refer to the MEGA-BOND brochure or visit www.ebaa.com.

*To learn more about this addendum, please visit: https://ebaa.com/spec/dip